## Sheet1
Life Safety Code Quality Assurance Plan
This document can be used as guidance to review life safety code compliance. Frequencies can be modified to fit organizational needs. You will find important notes and links on compliance throughout the guidance. Each row is listed individually to allow you to sort various ways including by frequency or category.
Category | Task | Frequency | Important Notes
Locked and Delayed Egress Doors | Assure that provider has a documented clinical needs assessment for locked doors, including memory care units and delayed egress doors. | Once | This could be incorporated as part of the facility assessment; however, ensure that the individual completing the life safety code walk-through knows that it is included in the facility assessment and is able to provide it to the surveyor.
Locked and Delayed Egress Doors | Codes are posted for magnetically locked doors for those with intact cognition that may need to exit in the event of an emergency. | Weekly | This can be accomplished in a variety of formats including individually given to the visitor/resident upon entrance, posted conspicuously in a picture but the key is ensuring that visitors and residents know where to find it. Note: it is not compliant if staff are the only ones who know the code. Frequencies could be decreased if no concerns are identified.
Locked and Delayed Egress Doors | Delayed egress doors have a sign with instructions on how to open the door. Typically, this includes "Push for 15 seconds, alarm will sound, and door will open." | Once | One the sign is verified in place, this could likely be a quarterly, semi-annual, or annual verification that the sign is still present. Notes: the sign must stand out (for example red lettering on clear door) and must be at an appropriate height to be visibly accessible.
Locked and Delayed Egress Doors | Delayed egress or locked doors must automatically release when the fire alarm sounds. | Monthly | This should be tested whenever the fire alarm is tested.
Locked and Delayed Egress Doors | Doors with locks should be single motion exit. | Semi-annual | Ensure that all locks on doors do not require two-motions to open such as twist type locks where you twist the lock and then have to turn the knob or deadbolt locks. It is good to maintain this as an ongoing monitor to ensure as door knobs are changed they remain compliant. This requirement includes office doors.
Maintaining Path of Egress | Ensuring there is no clutter in emergency exits such as hallways, stairwells, etc. | Daily
Maintaining Path of Egress | Ensuring that emergency exit doors are easily opened, without the use of excessive force. | Monthly
Maintaining Path of Egress | Ensuring that the pathway to the public sidewalk or area is free of hazards such as chipped concrete, heaved concrete, etc. | Monthly
Emergency Lights | Ensure that each emergency light has 2 bulbs installed as required. | Monthly
Emergency Lights | Functional testing is completed monthly. | Monthly | Each light must be individually listed, should include date, and who completed the testing on the form.
Emergency Lights | Annual Testing | Annual | Testing is conducted for not less than 90-minutes and each light must be individually listed on the documentation. The form should indicate that this is the annual testing, date, times, and who conducted the testing.
Emergency Lights | Medication room lights | Once | The medication room(s) light cannot be controlled by a switch. If the light is controlled by a switch (allowing the light to be turned off) then emergency lights must be present in the room.
Exit Signs | Exit signs are installed above all emergency exit doors as required in the blueprints. | Annual | Ensure all emergency exits have an exit sign with accuate directional signage (for example the directional arrow faces the actual direction of the emergency exit).
Exit Signs | Functional testing | Monthly | Functional testing must be conducted monthly and include documentation of each individually listed exit sign, date, and who completed.
Exit Signs | Annual Testing | Annual | Annual testing must be completed for no less than 90-minutes and each sign must be individually listed on the documentation including the date, start and stop times, and who completed the testing.
Hazardous Rooms/Self-Closure Devices | All doors of hazardous rooms must have a self-closing device installed on the door. | Semi-annual | This includes areas such as kitchens, mechanical rooms, soiled utility, laundry, and storage rooms. Note that a storage room is defined as a room over 50 ft2 that has items stored inside it. When initially completed, you should periodically monitor to ensure that devices were not removed and are still functional. Also, monitor rooms to ensure that new rooms were not transitioned into a storage room and would require a self-closing device.
Self-Closure Devices | Ensure that all doors with a self-closing device fully closes and positively latches. | Quarterly | If a door with a self-closing device does not fully close and latch, the self-closing device may need adjusted or the latching hardware may have malfunctioned and need repaired/replaced.
Self-Closure Devices | Doors with self-closing devices are only held open if the device is interconnected to the fire alarm system. | Ongoing | Devices such as wedges, buckets, carts, chairs, etc. cannot be used to hold-open a door.
Self-Closure Devices | Doors with self-closing devices that are interconnected to the fire alarm system release when the fire alarm system is tested. | Monthly | This should be tested whenever the fire alarm is tested.
All doors | Doors must fully close and positively latch without the use of excessive force. | Monthly | Doors that don't fully close and latch may allow for the passage of smoke and fire.
All doors | Monitor doors for gaps between the door and the door frame. | Monthly | Gaps between the door and frame may allow for the passaage of smoke and fire. This may require adjusting or replacing the door.
All doors | Ensure that all doors don't have penetrations or holes. | Monthly | Ensure that you include inspecting around door handles and knobs.
Fire Rated Doors | Doors that are fire rated must be inspected and tested annually. | Annual | Testing and inspection must be conducted by a qualified individual. You can find training to become a qualified individual on the NFPA website: https://www.nfpa.org/product/nfpa-80-fire-doors-and-fire-and-smoke-dampers-online-training-series/p0080olfd. Additionally, testing and inspection must include all required elements as outlined in the NFPA: https://www.nfpa.org/codes-and-standards/nfpa-80-standard-development/80
Alcohol-Based Hand Rub (ABHR) | Dispensers must not be installed near (within 1 inch) or above an ignition source (such as light switches and outlets). | Quarterly
Alcohol-Based Hand Rub (ABHR) | Dispensers must not be installed in corridors less than 6 feet wide | Quarterly
Alcohol-Based Hand Rub (ABHR) | Dispensers must not be installed over carpet, unless the area is fully sprinklered. | Quarterly
Alcohol-Based Hand Rub (ABHR) | Dispensers must have at least 4 foot of horizontal spacing. | Quarterly
Alcohol-Based Hand Rub (ABHR) | Each individual dispenser only holds 0.32 gallons of fluid or 18 oz of level 1 aerosol. | Quarterly
Alcohol-Based Hand Rub (ABHR) | There is not more than an aggregate of 10 gallons of fluid or 1135 oz of aerosol in a single smoke compartment outside of a storage cabinet (excluding one individual dispenser per room). | Quarterly
Alcohol-Based Hand Rub (ABHR) | Storage in a single smoke compartment shall not exceed 5 gallons unless compliance is met with NFPA 30. | Quarterly
Alcohol-Based Hand Rub (ABHR) | ABHR must not exceed 95% alcohol concentration. | Quarterly
Alcohol-Based Hand Rub (ABHR) | ABHR must be protected from inappropriate access. | Quarterly
Hood Suppression System(s) | Filters are installed vertically. | Weekly | Could be delegated to dietary staff.
Hood Suppression System(s) | Nozzles do not have excessive grease, dust, or debris buildup. | Monthly | If excessive grease buildup becomes a problem, more frequent cleaning services may be necessary.
Hood Suppression System(s) | Semi-annual inspections | Semi-annual | Ensure that reports of the report are maintained and include all required elements (pay close attention to ensure the report indicates the system is interconnected to the fire alarm system and any identified deficiencies are corrected). If deficiencies are identified, apply for a waiver while awaiting repair and retesting.
Hood Suppression System(s) | Monthly visual inspections | Monthly | Similar to portable fire extinguishers, the hood suppression system must be visually inspected and documented.
Hood Suppression System(s) | Cleaning reports | Semi-annual | Ensure that cleaning reports or invoices are maintained as proof of service.
Fire Alarm Pull Stations | Installation of pull stations shall not exceed more than 48 inches above the floor. | One-time
Fire Alarm Breaker | Must be mechanically protected and marked. | Quarterly
Audible/visible strobes | All common areas (including enclosed courtyards) must have audible and visible fire alarm notification devices to alert residents and staff of fire alarm activation. | One time | Enclosed courtyards include areas that require re-entry to the building in order to leave the area. A gated courtyard with an exit gate would not be considered enclosed for the purposes of this requirement.
Audible/visible strobes | Outdoor audible and visible strobes must be installed to alert fire department responders of alarm activation. | One time
Audible/visible strobes | Strobes must be synchronized | Semi-annual | This will be observed during fire alarm testing.
Smoke Detectors | Installed at least 3 feet from air supply. | One time
Smoke Detectors | Sensitivity testing completed every 2 years. | Annual | Verify documentation of testing is present. Documentation must include ranges of sensitivity that are considered "pass".
Fire/Smoke Dampers | Must be inspected every 4 years. | Annual | Ensure documentation is present.
Fire alarm system | Inspections | Semi-annual | Completed and documentation present.
Fire alarm system | Documentation lists all devices individually that are interconnected to the system. | Semi-annual
Fire alarm system | Deficiencies identified in the inspection report are corrected. | Semi-annual | Need to apply for a waiver if there is a deficiency in the system while awaiting repair and retesting.
Fire Alarm Notification | Phone line disruption | Monthly | There should be a process in place if there is interruption in phone service to determine how the signal is being transmitted to the monitoring company. Plans should address procedures on when phone lines are out of service.
Heat Detectors | Must be replaced every 15 years or according to manufacturer's recommendations. | Annual | Review recommendations with fire alarm monitoring company.
Fire Pump | Fire pump must be inspected as outlined in the template policy. | Monthly | Ensure documentation is present of required testing/inspections. . Sample policy and form can be located here: Policy - https://www.leadingageiowa.org/assets/Fire%20Pumps%20Inspection%20Testing%20and%20Maintenance%20-%20IA%20-%20IL.docx. Form - https://www.leadingageiowa.org/assets/Fire%20Pump%20Inspection%20%20Testing%20Form%20IA-%20IL.docx.
Fire Alarm System Outage | Policy and procedure available and includes all required elements including fire watch policy. | Annual | See policy template: Iowa - https://www.leadingageiowa.org/assets/Fire%20Alarm%20System%20Outage%20Policy.docx.
Sprinkler System Outage Policy | Policy and procedure available and includes all required elements including fire watch policy. | Annual | See Policy Template: Iowa - https://www.leadingageiowa.org/assets/Sprinkler%20System%20Outage%20Policy.docx.
Sprinkler System | Quarterly Inspections | Quarterly | Ensure documentation is present of the inspection and if any deficiencies are identified that they are corrected. If deficiencies need corrected request a waiver until they are repaired and retested.
Sprinkler System | Dry sprinkler system air leakage inspection | Annual | Completed at least every 3 years. Ensure documentation is present. *If air leakage testing is due during winter months request a waiver to complete during warm months to prevent pipes from freezing.
Sprinkler System | Internal obstruction inspections | Annual | Completed at least every 5 years. Ensure documentation is present.
Sprinkler System | There must be spare sprinkler heads in the red box in a quantity of not less than 6 of each type of sprinkler head used in the building. Also, you must have a sprinkler head wrench in the box for each type of sprinkler head used. | Annually
Sprinkler System | Sprinkler heads must be the same type in same rooms. | Annual
Sprinkler System | Cleanliness | Quarterly | Sprinkler heads must be free of excessive dirt, dust, debris. Sprinkler heads can be cleaned from these items, but if they have paint on the sprinkler head it must be replaced. Ensure also free of corrosion or rust.
Sprinkler System | Escutcheon Rings | Quarterly | Escutcheon rings must be present to ensure there are not gaps or penetrations around the sprinkler heads. The rings must be flush with the ceiling or wall.
Sprinkler System | Sprinkler head replacement | Annual | Dry sprinkler system heads must be replaced every 10 years, wet system every 50 years.
Sprinkler System | Storage of items near sprinkler heads | Quarterly | No items can be stored within 18 inches of sprinkler heads.
Sprinkler System | Air compressor for dry system | Annual | The air compressor for a dry sprinkler system must be hard wired into the electical system to ensure no one can unplug the compressor.
Sprinkler System | Gauges must be inspected or replaced at least every 5 years | Annual | Ensure documentation is present annually.
Sprinkler System | Visually inspect pipes to ensure no items are attached/affixed or stored on the sprinkler pipes. | Quarterly | Zip-ties and cables are commonly cited items.
Sprinkler System | The hydraulic name plate must be attached to the sprinkler riser. | Annual
Fire Safety Plan | Verify that the fire safety plan includes the required elements: outlines all types of extinguishment including sprinklers, portable extinguishers, hood suppression system; evacuation plans are addressed by smoke zones, vertically, zone of origin, and safe destination upon evacuation; preparation of floors for evacuation; use of alarms to notify of a fire including the appropriate response to the alarms; isolating the fire; transmission of the alarm signal to the fire department and who will call emergency services to ensure they are aware, a backup communication plan. | Annual
Fire Drills | Must be conducted on each shift once per quarter. | Quarterly | Best Practice - establish a schedule each year for fire drills including which shift during what months and the time frames each drill will be conducted.
Fire Drills | Drills must not be conducted at "approximately the same time". | Quarterly | Example - space drills so they are conducted during the even hours to ensure adequate distance.
Fire Drills | Circumstances of the fire drills must vary. | Quarterly | Example - drills can be electrical, grease, combustion, and located in various areas of the building.
Fire Drills | Silent drills can only be completed between 9 p.m. and 6 a.m. and the fire alarm must be checked the following day. | Quarterly
Fire Drills | Documentation includes all required elements such as details from the drill (date, time, location, person conducting, information on the fire - electrical, combustible, etc, did the alarm sound, did the alarm transmit to the monitoring company, any concerns identified, participants). | Monthly | According to life safety code surveys, when the monitoring company is contacted you should document their operator number/id/name.
Portable Fire Extinguishers | Visual inspections must be completed monthly to ensure that tampers and intact and current and the pressure is still adequate. | Monthly | Document completion on the tag. If you do not document on the tag you must have documentation that includes all required information.
Portable Fire Extinguishers | Inspection/Servicing must be conducted by an approved vendor. Ensure that you retain the tags from the visual inspections as evidence they were inspected. | Annual
Portable Fire Extinguishers | Portable extinguishers must be present within 30 feet of portable cooking devices | as needed | Example - portable popcorn machine.
Portable Fire Extinguishers | Fire extinguishers are mounted in a hangar and are readily accessible. | Monthly | Ensure that items are not stored in front of the fire extinguisher that would limit access in an emergency.
Portable Fire Extinguishers | There must be a K-type placard present near the k-type extinguisher that includes instructions on use. | Monthly | Verify the placard is present.
Penetrations | Observe smoke barriers for penetrations and repair when identified with fire proof caulk. | Monthly | This includes smoke barrier walls, corridor walls, ceilings, doors (essentially anything that would allow for the passage of smoke from one area to another).
Penetrations | Observe fire rated walls/doors for penetrations, repair as able and replace when necessary. | Monthly | Partricularly important if you have different levels of care that are interconnected.
Dryer Vents | The dryer vent tubing must be intact and affixed to the vent pipe. Any cracks in the vent tubing must be repaired with vent tape. | Monthly | Note that duct tape cannot be used. Visualize laundry area to ensure there isn't excessive lint from the dryer collecting that would increase fire hazards.
Electrical | Visualize all light switches, outlets, junction boxes for exposed wiring. This includes broken or missing cover plates. | Monthly | Depending on if this is problematic you may need to increase the frequency.
Electrical | Surge Protectors must be used for non-patient care related equipment (such as personal electronics). When used, they must meet UL1363A. If a power strip is used in non-patient care areas, they must be UL 1363. | Monthly
Electrical | Extension cords, multi plug adaptors, power strips, etc. cannot be used. | Monthly
Electrical | Outlets within 6 feet of a water source must be GFCI protected. | Annually
Electrical | GFCI outlets must trip when tested. | Monthly | Replace the outlet if it fails testing.
Electrical | Non-hospital grade outlets must be tested annually. Documentation must individually list each outlet and include continuity, ground, polarity, retention, date and who completed. | Annually | Ensure that retention values are documented and not just a check mark.
Electrical | When a non-hospital grade outlet fails testing they must be replaced with a hospital grade outlet. | As needed.
Electrical | Hospital grade outlets must be tested upon installation and with any repairs. | Annually | Ensure documentation is present.
Electrical | Patient-Care Related Electrical Equipment (PCREE) must be tested when put into service, with any repairs, and at a frequency identified by the provider but no less than annually. | Annually
Electrical | You must have a policy on PCREE testing. | On-time
Emergency Generators | Must complete weekly inspections of the emergency generator that includes fuel level (diesel), battery, oil, belts, and hoses. | Quarterly | Ensure documentation of weekly inspections is completed.
Emergency Generators | Monthly conduct a 30-minute load test that includes date, start and stop times, meter reading, transfer switch operation, amperage at each leg that must be at least 30% of the nameplate rating. | Quarterly | Ensure documentation of monthly load tests is completed.
Emergency Generators | Annually you must conduct testing and inspection of the Emergency Electrical System Main and Feeder Circuit breakers. | Annually
Emergency Generators | Diesel Fuel Generators require an annual fuel quality test. | Annually | If the test was not passed, documentation must include mitigation action.
Emergency Generators | Diesel fuel generators require a 1.5 hour load bank test annually. | Annually
Emergency Generators | Natural gas generators must have a natural gas reliability letter included from the vendor. | Annually | Ensure that you have the letter and verify vendor will still honor it.
Remote Stops | Remote stops must be present for emergency generators and water heaters. These must not be in the same location as the device. | One-time
Life Support Services Risk Assessment | A risk assessment and supporting policy must be present to identify whether the nursing home has the capability to provide life support services and if they are provided. | One-time | To offer life support services, you must ensure that your EES will automatically transfer immediately.
Smoking | Ensure no-smoking signage is present at the main entrances of the building(s). | Quarterly
Smoking | Designated smoking areas (if present) must have a mental self-closing container for discarding used smoking materials. | Quarterly | Ensure that the self-closing device is functioning properly and the container is not over-filled.
Smoking | Garbage must not be placed in the container for discarding smoking materials and discarded smoking materials must not be placed in the garbage. | On-going
Smoking | Discarded smoking materials must not be on the ground. | On-going
Privacy Curtains and Blinds | All privacy curtains and blinds must be fire retardant. | Annually | Ensure all privacy curtains have fire retardant tags on them. No vinyl mini blinds are present as window furnishings.
Space Heaters | Space heaters (if used) may only be used in areas where staff are not sleeping. | As needed
Space Heaters | Heating elements on space heaters must not exceed 212 degrees Fahrenheit | As needed | Ensure that manuals are maintained on each space heater to review that the heating element is in compliance with regulations.
Oxygen | E-cylinders must be in a secure, upright holder. | Ongoing
Oxygen | Storage for e-cylinders must be identified as "full" and "empty" and cylinders must not be commingled. | Daily
Oxygen | Combustible materials cannot be stored within 5-feet of oxygen cylinders. | Monthly | If combustible materials are stored within 5-feet they must be stored in a fire-proof cabinet.
Oxygen | Training must be completed upon hire and annually for those who apply and use medical gases. | Monthly | Review that annual training was completed within the last 12 months and new hires have documentation of training.
Oxygen | Oxygen concentrators must be turned off when not in use, particularly if the resident leaves the room. | Ongoing
Oxygen | A policy must identify that only individuals appropriately trained in the maintenance and repair of medical gas equipment will do so. | Annually | Ensure that a policy is implemented and reviewed at least annually.