## Table 1
Life Safety Code Quality Assurance Plan
Use this document as guidance for tasks and frequencies for LSC quality assurance. Frequencies can be modified to fit individual organization needs.
| Task | Frequency | Notes
Locked and Delayed Egress Doors | Assure that the provider has a documented clinical needs assessment for locked doors including memory care and delayed egress. | One time | This could be incorporated in the facility assessment.
Locked and Delayed Egress Doors | Codes are posted for magnetically locked doors for those with intact cognition that may need to exit in the event of an emergency. | Weekly (if no problems are identified could likely extend frequency) | This can be in a variety of formats including individually given to the visitor/resident upon entrance, posted conspicuously in a picture as long as visitors/residents know where to find it.
Locked and Delayed Egress Doors | Delayed egress doors have a sign with instructions on how to open the door. Typically, this includes “Push for 15 seconds, alarm will sound, and door will open.” | Once the sign is established, this could likely be a quarterly, semi-annual, or annual verification sign is still present. | According to 2567 reports the sign must stand out – for example could be red lettering on a clear door.
Maintaining Path of Egress | Ensuring there is no clutter in the hallways when required for emergency egress. Anything in hall should be affixed to the wall or the floor. | Daily | This likely does not need to be a documented quality assurance monitor, however, could be a visual inspection and education if continued concerns.
Maintaining Path of Egress | Ensuring that the emergency egress doors are easily opened, without the use of excessive force. | Monthly
Maintaining Path of Egress | Ensuring that the surface is free of hazards such as chipped concrete, heaved concrete, etc. | Monthly
Self-Closure Devices on Doors | All doors that contain hazardous items and are over 50 ft2 require a self- closure device. | One time and As Needed | This likely requires a one-time task to ensure all doors have a self-closure device, however, if rooms are repurposed this will need to be reassessed.
Self-Closure Devices on Doors | Door with self-closure devices shall fully close and positively latch. | Quarterly | This will be an ongoing assessment to ensure that self- closure devices don’t need adjusted to ensure that the door fully closes and latches.
Self-Closure Devices on Doors | Doors with self-closure devices are not being held open or have devices installed to hold open unless they are interconnected to the fire alarm system. | One time for installed devices, ongoing for hold- open devices. | Examine doors that have self- closing devices to ensure they don’t have a kick down device, however, the need will be ongoing to ensure staff are not utilizing devices to hold these doors open.
Self-Closure Devices on Doors | If doors are held open with magnetic devices that are interconnected with the fire alarm, ensure that they release with testing the fire alarm. | Monthly with fire drills. | This could be added as a part of the fire drill documentation to ensure all doors release. This should include double smoke doors.
Door Locks | Doors with locks should not be a two-motion lock to allow for ease of egress. | One time and as needed. | Ensure that all locks on doors do not require twisting of the lock and the handle in order to egress. This can be completed as a one-time monitor and may be completed as needed when locks/handles are replaced.
All Doors | Doors should fully close and positively latch without excessive force. | Monthly | Ensure that all doors in the building fully close and positively latch in the door frame. This includes doors that are not identified above with self-closing devices.
All Doors | Ensure that doors throughout the building do not have gaps between the door and the door frame that would allow for passage of smoke. | Monthly | Doors should be adjusted/repaired or replaced that have gaps as necessary.
All Doors | Ensuring that all doors do not have any holes or penetrations (including around door handles). | Monthly | Doors with holes should be repaired (for example if around door handle) or replaced if it affects the integrity of the door.
Fire/Smoke Rated Doors | Doors that are fire/smoke rated should be annually tested or inspected including the 11 elements outlined in NFPA 80 | Annually | https://lai.memberclicks.net/assets/SC17-38-LSC.Fire%20and%20Smoke%20Door%20Annual%20Testing%20Requirements.pdf and https://www.nfpa.org/codes-and-standards/all-codes-and-standards/list-of-codes-and-standards/detail?code=80
Exit Signs | Exit signs are installed above all emergency exit doors as required in the blueprints. | Annually | Ensure all emergency exits have an exit sign with appropriate directional signage.
Exit Signs | Monthly functional testing as appropriate. | Monthly | Ensure documentation is complete. Each exit sign should be individually listed.
Exit Signs | Annual testing of emergency backup power for exit signage. | Annually | Documentation should be complete indicating annual testing and each exit sign should be individually listed.
Emergency Lights | Ensure that each emergency light has 2 bulbs installed as required. | Monthly
Emergency Lights | Functional Testing | Monthly | Documentation completed with each light listed individually on the form.
Emergency Lights | 90-minute test | Annual | Documentation completed with each light listed individually on the form. The form should indicate this is the 90-minute annual test.
Hood Suppression System | Filters are installed correctly | Weekly *could be delegated to dietary staff. | Should be installed vertically.
Hood Suppression System | Nozzles do not contain excessive grease buildup. | Monthly – may need more frequently if excess buildup is noted. | Frequency may vary depending on type of cooking done in kitchen.
Hood Suppression System | Visual fire extinguisher inspections | Monthly | Document on the associated tag.
Hood Suppression System | Inspections | Semi-annual | Ensure that reports are on file and review the reports to determine if there are any deficiencies noted that need repaired. If there are ensure that repairs are scheduled and documented. May require additional inspection to ensure correction. Also ensure that inspection notes that the system is interconnected to the fire alarm system.
ABHR Dispensers | ABHR dispensers must not be installed near or above an ignition source. (Includes light switches and outlets.) | Annual and as needed. | This likely only needs completed upon installation, however, would be good to check on an annual basis.
Manual Pull Stations | Installation is not more than 48 inches above the floor. | One time
Fire Alarm Breakers | Must be in a secured electrical panel to prevent being inadvertently turned off. | One time and as needed. | This may be a one-time monitor; however, it may be good to put on a routine checklist as well to ensure that the breakers remain secure.
Smoke Detectors | Installed greater than 3 feet from an air supply. | One time and as needed. | Smoke detectors must be installed at least 3 feet from an air supply including any vents.
Audible/visible Strobes in Common Areas | All common areas must have an audible/visible fire alarm strobe to alert residents and staff of fire alarm activation. | One time and as needed. | While this likely is a one time monitor it would be advised to ensure that this is included on the device lists for the fire alarm inspections.
Outdoor Audible/Visual Strobe | An outdoor audible/visual strobe must be installed to alert the fire department that the fire alarm system has been activated. | One time and as needed. | See above comments for common area.
Sensitivity Testing | Smoke detectors must have sensitivity testing completed. | Every 2 years. | Ensure completed and documentation on file.
Fire Dampers | Fire dampers must be inspected. | Every 4 years. | Ensure completed and documentation on file.
Fire Alarm Inspections | Semi-annual and Annual Inspections  Areas that did not pass are scheduled for repair and reinspected as necessary.  Reports include all devices that are interconnected to the fire alarm such as magnetic hold open devices, suppression systems, etc. | Every 6 months | Ensure that these are completed and documentation on file.
Fire Alarm Notification | Phone line disruption. | Monthly | There should be a process in place if there is interruption in phone service to determine how the signal is being transmitted to the monitoring company. Plans should address the backup procedures if phone lines are down.
Heat Detectors | Replaced every 15 years. |  | This is according to 2567 reports; however, I would discuss with fire alarm vendor to determine if this is required with specific fire alarm systems.
Fire Alarm System Outage | Policy and procedure include required elements including fire watch policy and procedure. | One time and as needed for changes. | Example policy: https://lai.memberclicks.net/assets/Fire%20Alarm%20System%20Watch%20Policy%2010-1-2018.pdf
Sprinkler System Outage | Policy and procedure include required elements including fire watch policy and procedure. | One time and as needed for changes. | Requirements: https://lai.memberclicks.net/assets/Sprinkler%20Outage%20Policy%20Requirements.pdf
Sprinkler System Inspections Check with vendor for manufacturer recommended inspections. | Internal Obstruction | Every 5 years. | Ensure documentation present. Correct and deficient practices.
Sprinkler System Inspections Check with vendor for manufacturer recommended inspections. | Quarterly/Annual/Semi- Annual Inspection | Quarterly | Ensure documentation present. Correct and deficient practices.
Sprinkler System Inspections Check with vendor for manufacturer recommended inspections. | Leakage | Every 3 years | Ensure documentation present. Correct and deficient practices.
Sprinkler Heads | Installation of like sprinkler heads in the same room/area. | One time and as needed. | Ensure that each room has the same type of sprinkler head installed.
Sprinkler Heads | Cleanliness | Monthly (potentially more frequently depending on dust in the building). | Looking for dust, lint, corrosion, grease, paint. Reminder – paint needs replaced.
Sprinkler Heads | Dry Barrel Sprinkler Heads | 10 years | If a dry sprinkler system is in place dry barrel sprinkler heads need replaced every 10 years. Check with inspection vendor to confirm.
Sprinkler Heads | Escutcheon Rings | Monthly | Verify placement of escutcheon rings on all applicable sprinkler heads.
Sprinkler Heads | Storage | Weekly | Items must be stored at least 18” from sprinkler heads.
Sprinkler System Gauges | Inspection and/or Replacement | 5 years | Gauges are required to be inspected or replaced every 5 years.
Sprinkler Pipes | Items attached to piping | Monthly | Verify that nothing is attached to the sprinkler piping that is not necessary for the functionality of the system. Examples - zip tied wires, storage items.
Sprinkler Riser | Hydraulic Name Plate | One time and as needed | The sprinkler riser should contain a hydraulic name plate.
Portable Fire Extinguisher - Inspections | Visual Inspection and ensuring that tampers are intact and current. | Monthly | Document on the tag.
Portable Fire Extinguisher - Inspections | Inspection/Servicing | Annual | Performed by vendor. Retain previous years tags for documentation verification of monthly visual inspection.
Portable Extinguisher | Present on portable cooking devices or within 30 feet. | As needed | Example – popcorn machine.
Portable Fire Extinguishers - Storage and Accessibility | Portable fire extinguishers are stored in a hangar and are readily accessible. | Monthly | Ensure that items are not stored in front of the fire extinguisher that would limit access in emergency.
K-type Placard | K-type portable extinguisher must have a placard present. | Monthly | The placard must state that the hood extinguishment system must be activated prior to using.
Penetrations | Observe smoke barriers for penetrations and repair when identified. | Monthly | This includes smoke barrier walls, corridor walls, ceilings, doors (essentially anything that would allow for the passage of smoke from one area to another)
Penetrations | Observe fire rated walls/doors for penetrations. Repair as able, replace when necessary. | Monthly | Particularly important if you have different levels of care that are interconnected.
Dryer Vents | The dryer vent tubing must be intact and affixed to the vent pipe. Any cracking in the vent tubing must be repaired with vent tape. | Monthly | Note that duct tape cannot be used for this.
Electrical | Observation of light switches, outlets, junction boxes for exposed wiring. This includes broken or missing cover plates. | Monthly – depending on if this is problematic may need to increase frequency. | No electrical wires should be exposed.
Surge Protectors and Extension Cords - Resources: https://dps.iowa.gov/sites/default/files/state-fire-marshal/fire-prevention/surgeprotectorpolicyhealthcare.pdf | Only UL approved power strips can be utilized based on location being used. This includes surge protectors, extension cords, multi-plug adaptors and appliances with built in plugs. UL approved power strips cannot be piggybacked. | Bi-monthly | Only approved devices can be plugged into UL approved power strips. Prohibited items include but are not limited to: Lift Chairs; Adjustable beds; Lamps; Electronic Charging Devices; Battery Chargers; Warming Pots; Air Diffusers; Refrigerators; A/C Units; Electric Heaters; Mircowaves; Decorative Lights; Hair Dryers; Curling Irons; Oxygen Concentrators; Paper Shredders; Keurig; Water Coolers.
GFCI Outlets | Installed near water sources. | Annually | Ensure that if an outlet is near a water source that it is GFCI protected.
GFCI Outlets | GFCI trips when tested. | Monthly | Replace outlet if GFCI does not trip.
Electrical Outlet -Testing Resources: https://lai.memberclicks.net/assets/Electrical%20Outlet%20Testing%20Overview%20Sheet.pdf and https://lai.memberclicks.net/assets/Receptacle%20Testing%20Form.pdf | Testing of outlets based on grade (hospital vs. non- hospital). Documentation must include:  Outlets listed individually.  Continuity  Ground  Polarity  Retention  Pass/Fail  Comments | Annually and as needed | Non-hospital grade outlets must be tested annually, and hospital grade outlets require testing upon installation and repair (additional frequencies may be required). Comments should include if it was replaced. If replace should replace with hospital-grade outlet and re-test.
Patient-Care Related Electrical Equipment | Testing – when put into service and anytime the equipment is repaired. | When equipment put into service and upon repair. | Ensure that this is documented and contains all required elements. Example Form: https://lai.memberclicks.net/assets/patient%20care%20equipment%20testing%20and%20inspection%20form.docx
Patient-Care Related Electrical Equipment | Policy & Procedures | One-time and annually reviewed/updated | Develop policy and procedure on PCREE testing and inspection including process for testing. Example: https://lai.memberclicks.net/assets/Patient%20care%20equipment%20testing%20and%20inspection.docx
Fire Safety Plan | Includes required elements:  Different types of extinguishment including sprinklers, portable extinguishers, hood suppression system.  Evacuation Plans:  Smoke zones  Vertical  Zone of origin  Safe destination upon evacuation  Preparation of floors for evacuation  Addresses:  Use of alarms including response.  Isolation of the fire.  Transmission to the fire department.  Backup communication plan. | One time and annually reviewed/updated.
Fire Drills | Conducted each shift at least quarterly. | Quarterly | Review for:  Times vary (at least 1 hour separates other drills on same shift).  Circumstances vary.  Silent drills are only conducted between the hours of 9 p.m. and 6 a.m. with a daytime test of the alarm system.
Smoking | Proper disposal | Weekly | If smoking is allowed on the premises, there must be a metal ashtray with a self- closing lid present. Ensure that combustible items are not discarded in the approved ashtray. Ensure that smoking materials are not discarded in unapproved containers.
Smoking | Signage | Quarterly | Appropriate signage for “no smoking” should be displayed on main entrances.
Privacy Curtains and Blinds | All privacy curtains and blinds must be fire retardant. | Annually and as needed | Ensure all privacy curtains have fire retardant tags on them. No vinyl mini blinds are utilized to cover windows.
Space Heaters | Space heaters if used may only be used in areas where staff are not sleeping, and the heating elements must not exceed 212 degrees Fahrenheit. | Likely not necessary in the summertime but may require monthly or more frequent inspection in the winter. | Ensure that manuals are kept, to provide evidence that the space heater meets requirements.
Risk Assessment and Policy on Life Support Services | A risk assessment and supporting policy must be conducted. The provider must identify whether residents can be admitted with life support devices. | Annually | Conduct initially and review/update annually. Example: https://lai.memberclicks.net/assets/Life%20Support%20Services%20Risk%20Assessment%20Procedure%20and%20Statement.docx
Oxygen Storage | E-cylinders must be in a secure, upright holder. | Ongoing
Oxygen Storage | E-cylinder storage must be identified as “full” and “empty” | Labeling one time, monitor weekly | Full and empty cylinders must not be commingled.
Oxygen Storage | Cylinders stored within 5 feet of combustible materials. | Initially and monitor weekly. | Combustible materials include cardboard boxes and tubs that hold tubing and accessories.
Oxygen Training | Training must be conducted upon hire and annually for those that apply/use medical gases. | Monthly | Monthly to ensure that staff who assist with oxygen are trained on hire, annually to ensure that training is ongoing.
Oxygen Maintenance & Repair | A policy must identify that only individuals appropriately trained in the maintenance and repair of medical gas equipment will do so. | Initially and review/update annually. | No-one that is not adequately trained on repairing/maintenance of oxygen equipment should do so.
Oxygen Concentrators | Oxygen concentrators must be turned off when not in use, particularly when the resident leaves the room. | Ongoing
Emergency Generators - Inspections and Testing | Weekly visual inspections must include fuel level, battery, oil level, belts and hoses. | Quarterly | Ensure documentation present Generator Testing and Inspection Requirements: https://lai.memberclicks.net/assets/Generator%20Testing%20%20Inspection%20Requirements.pdf
Emergency Generators - Inspections and Testing | Monthly testing must include meter reading, transfer switch operation, date, start time, stop time, amperage and voltage at each leg tested to at least 30% of nameplate rating. | Quarterly | Ensure documentation present. Transfer switch time should not exceed 10 seconds. Spark ignited generators must be tested for 30 min
Emergency Generators - Inspections and Testing | Annual inspection and testing for main and feeder circuit breakers. | Annually | Ensure documentation present.
Emergency Generators - Inspections and Testing | Diesel fuel generators require an annual fuel test. | Annually | Document mitigation measures if failed.
Emergency Generators - Inspections and Testing | Diesel fuel generators require a 1.5-hour load bank test annually | Annually | Ensure documentation present.
Emergency Generator - Remote Stop | Emergency stop must be in a remote location. | One time | Cannot be installed in the same room.
Natural Gas Generators | Must have a natural gas reliability letter included from natural gas vendor. | One time – ensure present annually.